## Figure 7 - Event Tree
Figure 7 — Event Tree Analysis: BESS Thermal Runaway Propagation Sequence
EQIX SG4-4A Battery Room BESS ¦ NMC 485.52 kWh ¦ Two-Compartment Design
Initiating event: Multi-cabinet thermal runaway, P = 1.50 × 10⁻⁴/yr ¦ BMS detection → UL 9540A barrier → Suppression (Branch A water-only / Branch B gas+water)
| PREVENTION LAYERS | [5 empty] | SUPPRESSION STAGE |  |  | OUTCOMES & CONSEQUENCES
| INITIATING EVENT P = 1.50 × 10⁻⁴/yr |  | BMS DETECTION P(fail) = 0.15 |  | UL 9540A BARRIER P(fail) = 0.08 |  | Branch A: Water-only P(fail) = 0.622 | Branch B: Gas+Water P(fail) = 0.124 |  | Sc. | Outcome Description | Frequency [/yr] | Risk Category
| Multi-cabinet TR P = 1.50e-4/yr | → | YES (0.85) | → | ─ | ─ | ─ | ─ | ─ | 1 | No Propagation: TR limited to initiating cell | 1.28 × 10⁻⁴ | Broadly Acceptable
|  |  | NO (0.15) | ↓→
[5 empty] | YES (0.92) | → | ─ | ─ | ─ | 2 | Limited Propagation: UL 9540A contained spread to adjoining cabinet | 2.07 × 10⁻⁵ | Broadly Acceptable
[5 empty] | NO (0.08) | ↓→ | P_node = 1.80 × 10⁻⁶/yr (suppression branch point)
BRANCH A — Water-only design
[7 empty] | YES (p=0.378) | → | ─ | 3A | Flaming Controlled: water-only suppression effective | 6.80 × 10⁻⁷ | ALARP
[7 empty] | NO (p=0.622) | → | ─ | 4A | Uncontrolled Fire: HF release, full TR propagation | 1.12 × 10⁻⁶ | ALARP (upper tolerable)
BRANCH B — Gas+Water dual design
[7 empty] | YES (p=0.876) | → | ─ | 3B | Flaming Controlled: gas agent + water backup effective | 1.58 × 10⁻⁶ | Broadly Acceptable
[7 empty] | NO (p=0.124) | → | ─ | 4B | Residual Risk: both suppression systems fail | 2.23 × 10⁻⁷ | Broadly Acceptable
ERL COMPARISON — Worst-case outcomes (Scenarios 4A vs 4B per compartment)
| Design |  | P(suppression fails) |  | ERL [/yr] |  | P_individual |  | Risk Category
| Branch A — Water-only |  | 0.622 |  | 1.12 × 10⁻⁶ |  | 1 in 893,176/yr |  | ALARP (upper tolerable)
| Branch B — Gas+Water dual |  | 0.124 |  | 2.23 × 10⁻⁷ |  | 1 in 4,480,287/yr |  | Broadly Acceptable
ERL Reduction Branch B vs Branch A: 80.1% ¦ Voluntary dual suppression: ALARP → Broadly Acceptable
Source: BESS_Event_Tree.xlsx Monte Carlo PRA (N=10,000). All scenario frequencies reconcile with workbook.

## Figure 7 (High-Res PNG)
Figure 7 — Event Tree Analysis (rendered PNG, embedded)
Source: EQIX-SG4-4A_Figure7_EventTree.svg ¦ Rendered at 2800 × 1440 px