## Figure 13 - F-N Data
Figure 13 — Societal Risk F-N Curves: BESS Fire Scenarios
EQIX SG4-4A, Singapore ¦ NMC 485.52 kWh ¦ Two-Compartment Design ¦ Tolerance: UK HSE R2P2 (2001)
| Scenario | F(N≥1) [/yr] | F(N≥2) [/yr] | Individual Risk (1 in N/yr) | Reduction vs Branch A | HSE Classification
| 1-Compartment (hypothetical), Water-only | 2.5e-05 | 1.8e-06 | 1 in 40,000 | -19.0% lower | ALARP
| 2-Compartment, Water-only (Branch A) | 2.1e-05 | 1.5e-06 | 1 in 47,619 | — (baseline) | ALARP
| 2-Compartment, Gas+Water dual (Branch B) | 4.3e-06 | 3.1e-07 | 1 in 232,558 | 79.5% lower | Broadly Acceptable
| 2-Comp, Gas+Water + improved BMS (P=0.05) | 1.4e-06 | 1e-07 | 1 in 714,285 | 93.3% lower | Broadly Acceptable
Key Result: Adding voluntary gas suppression (Branch B vs Branch A) reduces F(N≥1) by 79.5%, crossing the broadly acceptable threshold.
HSE R2P2 (2001) Tolerance Criteria — Reference
| Zone | F(N≥1) threshold | F(N≥n) function | Action Required
| Intolerable | >10⁻³/yr | F > 10⁻³/N | Risk must be reduced (no exceptions)
| ALARP (Tolerable) | 10⁻⁵ to 10⁻³/yr | 10⁻⁵/N ≤ F ≤ 10⁻³/N | Reduce to As Low As Reasonably Practicable
| Broadly Acceptable | <10⁻⁵/yr | F < 10⁻⁵/N | No further reduction needed (monitor only)
Notes: F(N≥n) = complementary cumulative annual frequency. Occupant model: N_max=2 (operator + emergency responder), P_occ=0.15 per person, P_fatal ¦ uncontrolled flaming + HF = 0.825. Branch A baseline = 2-Comp Water-only (code minimum). Branch B = 2-Comp Gas+Water dual (voluntary). Source: BESS_Fire_Safety_Paper Section 4.6, Monte Carlo PRA N=10,000.

## Figure 13 (High-Res PNG)
Figure 13 — Societal Risk F-N Curves (rendered, embedded)
Source: matplotlib generation per Vrijling et al. (1995) and HSE R2P2 (2001) convention